## Instructions & Background (hidden)
Networked Lighting Control
Comments on DLC_NLCS_Spec_Draft_02-01-2017
Instructions
This Excel document lists 22 changes proposed in the draft Specification
DLC_NLCS_Spec_Draft_02-01-2017.docx
In the "Changes & Reviewer Comments" worksheet, enter your Organization, Name, Email Address and Phone Number at the top of the worksheet. Then enter any comments about specific changes in Column F, in the appropriate row for each of the numbered changes
Save the Excel file with your comments, with your initials appended to the end of the filename, and email the file to
info@DesignLights.org
by Monday March 6, 2017 COB.
Background
The DLC revises the Networked Lighting Controls Technical Requirements annually with final revisions completed on June 1 of each year.
Each Technical Requirements revision is distributed through the DLC stakeholder input process and comments will be considered for each revision. This begins in February of each year to allow sufficient time for stakeholder input to each proposed revision.
Each manufacturer must requalify and relist a system each year with the annual Technical Requirements revision schedule.
Grace Period Policy: A twelve month listing grace period will be provided for systems that have been qualified under a previous version of the Technical Requirements but do not meet revised requirements. This will allow a period of one year to revise a current system or offer a new system that qualifies according to the most current Technical Requirements.

## Changes & Reviewer Comments
Comment Report Form
Document: |  | Networked Lighting Control System Technical Requirements comments
Version: |  | Draft 1 of Version 3.0
Comments Due: |  | COB, Monday, Feb 26, 2018
Instructions and Background: |  | This document lists all of the proposed updates in the first draft of the 2018 DLC "Networked Lighting Control System Technical Requirements". To comment on these updates, enter your Organization, Name, Email Address and Phone Number at the top of the worksheet. Then enter any comments in Column F "Comment and Rationale". If applicable, please provide alternate approaches, technical justification, or data to support your comment; and responses to any questions posed in Column E "Explanation by DLC". Provide your proposed change corresponding to your comment in Column G "Proposed Change". Comments to the Technical Requirements that are not related to a specific revision the DLC has proposed may be added at the bottom of the worksheet. Save the Excel file with your comments, with your initials appended to the end of the filename, and email the file to info@designlights.org by COB, Monday, Feb 26, 2018.
|  |  | Reviewer Organization | Reviewer Name | Reviewer Email Address | Reviewer Phone #
Change | Location in TR (Line or Table & Row numbers) | Topic | Proposed Change in NLC Technical Requirements | Explanation by the DLC | Comment & Rationale | Proposed Change
1 | Lines 20-22 | DC/PoE | Accept Direct Current and Power over Ethernet systems. | These systems were formerly excluded because the DLC SSL (Solid State Lighting) QPL (Qualified Products List) excluded DC/PoE luminaires. DLC plans to accept DC/PoE luminaires on the SSL QPL in 2018, so this exclusion is removed.
2 | Lines 46-51 | Publicly Available Information | In order for an applicant to claim a capability, a reference to that capability must be available in public documentation. | A primary purpose of the QPL is to assist specifiers in product selection. If information about a particular capability is not publicly available to specifiers, contractors, or customers through an applicant’s documentation such as brochures, specification sheets or instruction manuals, then under this new proposal DLC will not list that system as having the capability. The intent of this new documentation requirement is to improve the documentation of listed systems. The DLC seeks to differentiate systems that provide documentation to their customers about their system's capabilities and how to implement them, versus systems that do not provide this documentation. As an example, some applicants have claimed the Demand Response capability because their system has a dry contact, but without any literature claiming that the system has Demand Response or describing how to implement the capability. Other applicants have developed robust how-to instructions for how to implement demand response with their system. Under the new proposed documentation requirement, the systems without documentation would no longer be listed as having Demand Response capability.
3 | Lines 65-67 | Presentations | For re-applications without major product updates, accept a recording from last year. | If a recorded presentation from last year is still applicable to the current product, then DLC reviewers can view that recording, in order to reduce the time and effort needed from the applicant.
4 | Lines 71-87, Table 3 Row 11 | Energy Monitoring | Phased approach: V3 in 2018: Ignore "calculated" values based on nominal or manual wattage V4 in 2019: Require Energy Monitoring | V3: Systems that calculate energy usage and savings based on nominal or manually entered wattage values are subject to human error. In addition, rarely are any specifiers, installers, or commissioning parties paid to ensure that wattage values are accurate or entered at all. Anecdotes and preliminary research suggest that errors of 15% to 40% are not unusual with these types of systems, and the step of entering the wattage values often does not happen. Utility efficiency programs have expressed a desire to no longer allow manually-entered "calculated" energy monitoring to qualify as energy monitoring within their programs. V4: Energy metering integrated circuits continue to become more widely available at lower cost. Efficiency programs can justify and support higher rebates and incentives, and ongoing performance rebates for continuous improvement, when the energy performance of NLC systems can be easily documented. Most networked lighting control systems available now include some form of energy monitoring, including lower cost simple room-based systems. Utility efficiency programs have expressed a desire to require that all eligible networked systems include energy monitoring capability. It should be noted that the technical requirements propose to require systems to have this capability, but not that it must be deployed on every project.
5 | Lines 88-99, Table 3 Row 20 | Security | Phased approach: V3 in 2018: Report UL 2900-1 V4 in 2019: Require UL 2900-1 or similar | Efficiency programs are concerned about the risk of providing rebates and incentives for networked systems that could be involved in security breaches. In addition, customer concerns about network security raise a significant market barrier to the broader adoption of NLC. The ANSI UL 2900 standard offers a reasonable way to address these concerns. It should be noted that if UL 2900-1:2017 appears to be too ambitious for full compliance across the lighting industry by 2019, then a lighting-industry-specific standard or a lighting specific version of ANSI UL-2900-1 could be developed that DLC could reference in 2019. A webinar introducing ANSI UL-2900 in the context of lighting controls is available here: https://industries.ul.com/events/lighting-systems-and-cybersecurity-are-your-systems-ready The ANSI UL 2900-1 standard is available for purchase here: https://standardscatalog.ul.com/standards/en/standard_2900-1_1
6 | Tables 1,2, Table 3 Row 23 | Scenes | Add Scene Control as a reported capability. | Some systems provide control of scenes, while others do not. This capability provides essential support for interoperability between systems from multiple vendors. Interoperability will support market expansion.
7 | Table 3 Row 19 | Emergency Lighting | Clarify description | Shorten, and replace "Interact" with "Connect", to more accurately describe the physical connections shown in a wiring diagram.
8 | Other | Other | For comments about other aspects of the Technical Requirements, please include the line number from the Technical Requirement or the Row number within a Table.
9
10
11
12
13
14
15
16
17
18
19